## HRSG 1
[33 empty] | Hot walkdown |  |  |  |  | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm)(+Y) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % error | Comments | Cold to Hot Travel (mm)(+Y)
L103H1 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 4 | 350-630-SH103-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-22-B1A-60 | - | 13CS3805 | SH103-15CJ1G-H-C001 | 2013-02 | 60 | - |  |  |  | 1439 kg | 1439 kg | -28 |  |  |  |  | 2022-09-20 | 49 | 64 |  |  | 2022-06-02 | 31 | 36 | 5 | -17.8571 |  | -18
L103H2 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-24-B1A-60 | - | 13CS3808 | SH103-15CJ1G-H-C002 | 2013-02 | 60 | - |  |  |  | 2064 kg | 2064 kg | 3 |  |  |  |  | 2022-09-20 | 34 | 49 |  |  | 2022-06-02 | 44 | 52 | 8 | 266.6667 |  | 10
L103H3 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE POSITION WITHIN RANGE BUT LIMITED MOVEMENT FROM COLD INDICATION POTENTIAL CLASH WITH STRUCTURE |  |  | SEONGHWA | CHH-9-F1-60 | - | 14CS1099 | SH103-15CJ1G-H-C003 | 2014-05 | 60 | - |  |  |  | 400 kg | 400 kg | 52 |  |  |  |  | 2022-09-20 | 92 | 47 |  |  | 2022-06-02 | 100 | 99 | 1 | 1.9231 | Likely bottomed out | 8
L103H4 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION POSITION DEVIATION POTENTIAL RESTRICTION AT DOWNSTREAM PIPE SUPPORT CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-36-B1A-80 | - | 13CS3811 | SH103-15CJ1G-H-C004 | 2014-05 | 80 | - |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-09-20 | 67 | 40 |  |  | 2022-06-02 | 62 | 60 | 2 | 10 |  | -5
L103H5E | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 2 | 350-630-SH103-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-28-B1A-60 | - | 14CS1098 | SH103-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | -18 |  |  |  |  | 2022-09-20 | 73 | 59 |  |  | 2022-06-02 | 55 | 41 | 14 | -77.7778 |  | -18
L103H5W | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-28-B1A-60 | - | 14CS1097 | SH103-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | -17 |  |  |  |  | 2022-09-20 | 82 | 59 |  |  | 2022-06-02 | 60 | 42 | 18 | -105.8824 |  | -22
L103H6 |  | SH103 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 215218 | - | 547400 | 630-SH180-PS-0-001 |  | 100 | 133.3 N/mm |  |  |  | - | 13.94 kN | -10 |  |  |  |  | 2022-09-20 | 68 | 65 |  |  | 2022-06-02 | 54 | 55 | 1 | -10 |  | -14
L115H1E | 300-630-SH115-15CJ1G-H | SH115 | V-2153-101-A-3006_004 | YES, 19 | 300-630-SH115-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG1 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1095 | SH115-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 17 |  |  |  |  | 2022-09-20 | 56 | 42 |  |  | 2022-06-02 | 43 | 59 | 18 | 105.8824 |  | -13
L115H1W | 300-630-SH115-15CJ1G-H | SH115 | V-2153-101-A-3006_004 | NO | 300-630-SH115-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG1 | BYPASS STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-24-B1A-60 | - | 14CS1096 | SH115-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-09-20 | 56 | 43 |  |  | 2022-06-02 | 39 | 58 | 19 | 126.6667 |  | -17
L115H2 |  | SH115 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 215218 | 586873 | - | 630-SH183-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.26 kN | -10 |  |  |  |  | 2022-09-20 | 32 | 30 |  |  | 2022-06-02 | 22 | 20 | 2 | -20 |  | -10
L115H3 |  | SH115 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 216218 | 547404 | - | 630-SH183-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.76 kN | -22 |  |  |  |  | 2022-09-20 | 73 | 87 |  |  | 2022-06-02 | 67 | 65 | 2 | -9.0909 |  | -6
L100H1 |  | SH100 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH2A-4-M20 | S130074-02 | 13VS8211 | SH102-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 18 |  |  |  |  | 2022-09-20 | 58 | 46 |  |  | 2022-06-02 | 67 | 64 | 3 | 16.6667 |  | 9
L101H1 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS8212 | SH101-HUL11-DN350-O02 | - | 100 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-09-20 | 36 | 12 |  |  | 2022-06-02 | 14 | 15 | 1 | 33.3333 |  | -22
L101H2 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH2F-4 | S130074-02 | 13VS8216 | SH101-HUL12-DN350-P10 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 13 |  |  |  |  | 2022-09-20 | 85 | 79 |  |  | 2022-06-02 | 91 | 92 | 1 | 7.6923 |  | 6
L101H3 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH3F-5 | S130074-02 | 13VS8217 | SH101-HUL12-DN350-P09 | - | 200 | 6.8 kg/mm |  |  |  | 1150 kg | 1326 kg | 26 |  |  |  |  | 2022-09-20 | 82 | 71 |  |  | 2022-06-02 | 98 | 97 | 1 | 3.8462 |  | 16
L101H4 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH3A-6-M30 | S130074-02 | 13VS8215 | SH101-HUL13-DN350-P14 | - | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 33 |  |  |  |  | 2022-09-20 | 20 | 15 |  |  | 2022-06-02 | 35 | 48 | 13 | 39.3939 |  | 15
L102H1 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-3-M16 | S130074-02 | 13VS8210 | SH102-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 353 kg | 418 kg | 8 |  |  |  |  | 2022-09-20 | 29 | 26 |  |  | 2022-06-02 | 31 | 34 | 3 | 37.5 |  | 2
L102H2 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS8213 | SH102-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1002 kg | 1220 kg | 8 |  |  |  |  | 2022-09-20 | 9 | 7 |  |  | 2022-06-02 | 12 | 15 | 3 | 37.5 |  | 3
L102H3 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-6-M30 | S130074-02 | 13VS8214 | SH102-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 9 |  |  |  |  | 2022-09-20 | 8 | 18 |  |  | 2022-06-02 | 13 | 27 | 14 | 155.5556 |  | 5
L102H4 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3833 | SH102-HUL21-DN350-AA25 | 2014-02 | 100 | - |  |  |  | 2658 kg | 2658 kg | -62 |  |  |  |  | 2022-09-20 | 76 | 81 |  |  | 2022-06-02 | 20 | 19 | 1 | -1.6129 |  | -56
L102H5 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3832 | SH102-HUL21-DN350-AA19 | 2014-02 | 100 | - |  |  |  | 2431 kg | 2431 kg | -59 |  |  |  |  | 2022-09-20 | 69 | 79 |  |  | 2022-06-02 | 26 | 20 | 6 | -10.1695 |  | -43
L102H6 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-20-B1A-120 | - | 13CS3831 | SH102-HUL21-DN350-AA21 | 2014-02 | 120 | - |  |  |  | 673 kg | 673 kg | -64 |  |  |  |  | 2022-09-20 | 70 | 83 |  |  | 2022-06-02 | 20 | 19 | 1 | -1.5625 |  | -50
L102H7 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-34-B1A-120 | - | 13CS3834 | SH102-HUL23-DN350-AA24 | 2014-02 | 120 | - |  |  |  | 2336 kg | 2336 kg | -63 |  |  |  |  | 2022-09-20 | 75 | 81 |  |  | 2022-06-02 | 19 | 18 | 1 | -1.5873 |  | -56
L102H8 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-30-F1-130 | - | PLATE MISSING | SH102-HUL26-DN350-AA23 | PLATE MISSING | 130 | - |  |  |  | 1656 kg | 1656 kg | -69 |  |  |  |  | 2022-09-20 | 69 | 69 |  |  | 2022-06-02 | 0 | 0 | 0 | 0 |  | -69
Note on U14: Alex Horner: This suggests the hanger belongs on line 102 not 100. Hanger is mislabeled?
Note on R26: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM OTHER HRSGs
Note on U26: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on W26: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on AB26: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on AC26: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT