## HRSG 1
[33 empty] | Hot walkdown |  |  |  |  | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % error | Comments
L103H1 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 4 | 350-630-SH103-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-22-B1A-60 | - | 13CS3805 | SH103-15CJ1G-H-C001 | 2013-02 | 60 | - |  |  |  | 1439 kg | 1439 kg | 28 |  |  |  |  | 2022-06-02 |  | 64 |  |  | 44714 | 31 | 36 | 5 | 17.8571
L103H2 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-24-B1A-60 | - | 13CS3808 | SH103-15CJ1G-H-C002 | 2013-02 | 60 | - |  |  |  | 2064 kg | 2064 kg | 3 |  |  |  |  | 2022-06-02 |  | 49 |  |  | 44714 | 44 | 52 | 8 | 266.6667
L103H3 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE POSITION WITHIN RANGE BUT LIMITED MOVEMENT FROM COLD INDICATION POTENTIAL CLASH WITH STRUCTURE |  |  | SEONGHWA | CHH-9-F1-60 | - | 14CS1099 | SH103-15CJ1G-H-C003 | 2014-05 | 60 | - |  |  |  | 400 kg | 400 kg | 52 |  |  |  |  | 2022-06-02 |  | 47 |  |  | 44714 | 100 | 99 | 1 | 1.9231 | Likely bottomed out
L103H4 | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION POSITION DEVIATION POTENTIAL RESTRICTION AT DOWNSTREAM PIPE SUPPORT CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-36-B1A-80 | - | 13CS3811 | SH103-15CJ1G-H-C004 | 2014-05 | 80 | - |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-06-02 |  | 40 |  |  | 44714 | 62 | 60 | 2 | 10
L103H5E | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 2 | 350-630-SH103-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-28-B1A-60 | - | 14CS1098 | SH103-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-02 |  | 59 |  |  | 44714 | 55 | 41 | 14 | 77.7778
L103H5W | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 13 | 350-630-SH103-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG1 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-28-B1A-60 | - | 14CS1097 | SH103-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 17 |  |  |  |  | 2022-06-02 |  | 59 |  |  | 44714 | 60 | 42 | 18 | 105.8824
L103H6 |  | SH103 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 215218 | - | 547400 | 630-SH180-PS-0-001 |  | 100 | 133.3 N/mm |  |  |  | - | 13.94 kN | 8.93 |  |  |  |  | 2022-06-02 |  | 65 |  |  | 44714 | 54 | 55 | 1 | 11.1982
SNUBBER | 350-630-SH103-15CJ1G-H | SH103 | L630-DX-ISO-10528.001 | YES, 8 | 350-630-SH103-15CJ1G-H-X001 | V-2153-101-A-8006_002 | HRSG1 | MAIN STEAM | SNUBBER | [5 empty] | SANWA | [17 empty] | 2022-06-02
L115H1E | 300-630-SH115-15CJ1G-H | SH115 | V-2153-101-A-3006_004 | YES, 19 | 300-630-SH115-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG1 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1095 | SH115-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 17 |  |  |  |  | 2022-06-02 |  | 42 |  |  | 44714 | 43 | 59 | 18 | 105.8824
L115H1W | 300-630-SH115-15CJ1G-H | SH115 | V-2153-101-A-3006_004 | NO | 300-630-SH115-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG1 | BYPASS STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE CORROSION CLARIFY TRAVEL STOP FIXING ARRANGEMENT |  |  | SEONGHWA | CHH-24-B1A-60 | - | 14CS1096 | SH115-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-06-02 |  | 43 |  |  | 44714 | 39 | 58 | 19 | 126.6667
L115H2 |  | SH115 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 215218 | 586873 | - | 630-SH183-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.26 kN | 9.56 |  |  |  |  | 2022-06-02 |  | 30 |  |  | 44714 | 22 | 20 | 2 | 20.9205
L115H3 |  | SH115 |  |  |  |  | HRSG1 | [7 empty] | LISEGA | 216218 | 547404 | - | 630-SH183-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.76 kN | 21.79 |  |  |  |  | 2022-06-02 |  | 87 |  |  | 44714 | 67 | 65 | 2 | 9.1785
L100H1 |  | SH100 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH2A-4-M20 | S130074-02 | 13VS8211 | SH102-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 16 |  |  |  |  | 2022-06-02 |  | 46 |  |  | 44714 | 67 | 64 | 3 | 18.75
L101H1 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS8212 | SH101-HUL11-DN350-O02 | - | 100 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-06-02 |  | 12 |  |  | 44714 | 14 | 15 | 1 | 33.3333
L101H2 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH2F-4 | S130074-02 | 13VS8216 | SH101-HUL12-DN350-P10 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 13 |  |  |  |  | 2022-06-02 |  | 79 |  |  | 44714 | 91 | 92 | 1 | 7.6923
L101H3 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH3F-5 | S130074-02 | 13VS8217 | SH101-HUL12-DN350-P09 | - | 200 | 6.8 kg/mm |  |  |  | 1150 kg | 1326 kg | 26 |  |  |  |  | 2022-06-02 |  | 71 |  |  | 44714 | 98 | 97 | 1 | 3.8462
L101H4 |  | SH101 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH3A-6-M30 | S130074-02 | 13VS8215 | SH101-HUL13-DN350-P14 | - | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 31 |  |  |  |  | 2022-06-02 |  | 15 |  |  | 44714 | 35 | 48 | 13 | 41.9355
L102H1 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-3-M16 | S130074-02 | 13VS8210 | SH102-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 353 kg | 418 kg | 8 |  |  |  |  | 2022-06-02 |  | 26 |  |  | 44714 | 31 | 34 | 3 | 37.5
L102H2 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS8213 | SH102-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1002 kg | 1220 kg | 8 |  |  |  |  | 2022-06-02 |  | 7 |  |  | 44714 | 12 | 15 | 3 | 37.5
L102H3 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | VH1A-6-M30 | S130074-02 | 13VS8214 | SH102-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 8 |  |  |  |  | 2022-06-02 |  | 18 |  |  | 44714 | 13 | 27 | 14 | 175
L102H4 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3833 | SH102-HUL21-DN350-AA25 | 2014-02 | 100 | - |  |  |  | 2658 kg | 2658 kg | 62 |  |  |  |  | 2022-06-02 |  | 81 |  |  | 44714 | 20 | 19 | 1 | 1.6129
L102H5 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3832 | SH102-HUL21-DN350-AA19 | 2014-02 | 100 | - |  |  |  | 2431 kg | 2431 kg | 59 |  |  |  |  | 2022-06-02 |  | 79 |  |  | 44714 | 26 | 20 | 6 | 10.1695
L102H6 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-20-B1A-120 | - | 13CS3831 | SH102-HUL21-DN350-AA21 | 2014-02 | 120 | - |  |  |  | 673 kg | 673 kg | 64 |  |  |  |  | 2022-06-02 |  | 83 |  |  | 44714 | 20 | 19 | 1 | 1.5625
L102H7 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-34-B1A-120 | - | 13CS3834 | SH102-HUL23-DN350-AA24 | 2014-02 | 120 | - |  |  |  | 2336 kg | 2336 kg | 63 |  |  |  |  | 2022-06-02 |  | 81 |  |  | 44714 | 19 | 18 | 1 | 1.5873
L102H8 |  | SH102 |  |  |  |  | HRSG1 | [7 empty] | SEONGHWA | CHH-30-F1-130 | - | PLATE MISSING | SH102-HUL26-DN350-AA23 | PLATE MISSING | 130 | - |  |  |  | 1656 kg | 1656 kg | 69 |  |  |  |  | 2022-06-02 |  | 69 |  |  | 44714 | 0 | 0 | 0 | 0
Note on U15: Alex Horner: This suggests the hanger belongs on line 102 not 100. Hanger is mislabeled?
Note on R27: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM OTHER HRSGs
Note on U27: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on W27: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on AB27: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT
Note on AC27: Alex Horner: PLATE MISSING! VALUE ASSUMED FROM CONTEXT

## HRSG 2
[33 empty] | Hot walkdown | [5 empty] | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | % error | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % error | Comments
L203H1 | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | SURFACE COATING DAMAGE |  |  | SEONGWHA | CHH-22-B1A-60 | - | 13CS3814 | SH203-15CJ1G-H-C001 | 2013-02 | 60 | - |  |  |  | 1439 kg | 1439 kg | 29 |  |  |  |  | 2022-05-31 | 57 | 64 | 7 | 24.1379 |  | 2022-07-08 | 39 | 35 | 4 | 13.7931
L203H2 | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | CORROSION LOOSE NUT |  |  | SEONGWHA | CHH-24-B1A-60 | - | 13CS3817 | SH203-15CJ1G-H-C002 | 2013-02 | 60 | - |  |  |  | 2064 kg | 2064 kg | 3 |  |  |  |  | 2022-05-31 | 41 | 49 | 8 | 266.6667 |  | 2022-07-08 | 54 | 52 | 2 | 66.6667
L203H3 | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | No | YES | MISSING SLIDE PLATE POTENTIAL MOVEMENT RESTRICTION DUE TO PERSONNEL PROTECTION |  |  | SEONGWHA | CHH-9-F1-60 | - | 14CS1104 | SH203-15CJ1G-H-C003 | 2014-05 | 60 | - |  |  |  | 400 kg | 400 kg | 54 |  |  |  |  | 2022-05-31 | 95 | 46 | 49 | 90.7407 |  | 2022-07-08 | 100 | 100 | 0 | 0
L203H4 | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGWHA | CHH-36-B1A-80 | - | 13CS3820 | SH203-15CJ1G-H-C004 | 2014-05 | 80 | - |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-05-31 | 63 | 40 | 23 | 115 |  | 2022-07-08 | 59 | 60 | 1 | 5
L203H5E | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGWHA | CHH-28-B1A-60 | - | 14CS1103 | SH203-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 19 |  |  |  |  | 2022-05-31 | 43 | 59 | 16 | 84.2105 |  | 2022-07-08 | 22 | 40 | 18 | 94.7368
L203H5W | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 4 | 350-630-SH203-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG2 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGWHA | CHH-28-B1A-60 | - | 14CS1102 | SH203-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 19 |  |  |  |  | 2022-05-31 | 47 | 59 | 12 | 63.1579 |  | 2022-07-08 | 24 | 40 | 16 | 84.2105
L203H6 |  | SH203 |  |  |  |  | HRSG2 | [7 empty] | LISEGA | 215218 | 547404 | - | 630-SH280-PS-0-001 |  | 100 | 133.3 N/mm |  |  |  | - | 14.1 kN | 7.92 |  |  |  |  | 2022-05-31 | 79 | 67 | 12 | 151.5152 |  | 2022-07-08 | 52 | 55 | 3 | 25
SNUBBER | 350-630-SH203-15CJ1G-H | SH203 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH203-15CJ1G-H-X001 | V-2153-101-A-8006_002 | HRSG2 | MAIN STEAM | SNUBBER | [5 empty] | SANWA | [12 empty] | 0 |  |  |  |  | 2022-05-31 | [5 empty] | 2022-07-08 |  |  | 0 | #DIV/0!
L215H1E | 300-630-SH215-15CJ1G-H | SH215 | V-2153-101-A-3006_004 | NO | 300-630-SH215-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG2 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGWHA | CHH-24-B1A-60 | - | 14CS1101 | SH215-15CJ1G-H-C001 | 2014-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-05-31 | 69 | 43 | 26 | 173.3333 |  | 2022-07-08 | 58 | 58 | 0 | 0
L215H1W | 300-630-SH215-15CJ1G-H | SH215 | V-2153-101-A-3006_004 | YES, 4 | 300-630-SH215-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG2 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGWHA | CHH-24-B1A-60 | - | 14CS1100 | SH215-15CJ1G-H-C001 | 2014-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-05-31 | 64 | 43 | 21 | 140 |  | 2022-07-08 | 50 | 58 | 8 | 53.3333
L215H2 |  | SH215 |  |  |  |  | HRSG2 | [7 empty] | LISEGA | 215218 |  | - | 630-SH283-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.52 kN | 7.58 |  |  |  |  | 2022-05-31 | 25 | 28 | 3 | 39.5778 |  | 2022-07-08 | 16 | 20 | 4 | 50
L215H3 |  | SH215 |  |  |  |  | HRSG2 | [7 empty] | LISEGA | 216218 | 547404 | - | 630-SH283-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.53 kN | 22.77 |  |  |  |  | 2022-05-31 | 69 | 87 | 18 | 79.0514 |  | 2022-07-08 | 61 | 65 | 4 | 18.1818
L200H1 |  | SH200 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH2A-4-M20 | S130074-02 | 13VS8219 | SH202-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 16 |  |  |  |  | 2022-05-31 | 58 | 46 | 12 | 75 |  | 2022-07-08 | 66 | 63 | 3 | 17.6471
L201H1 |  | SH201 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH1A-5-M24 | S130074-02 | 13VS8220 | SH201-HUL11-DN350-O02 | - | 50 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-05-31 | 12 | 12 | 0 | 0 |  | 2022-07-08 | 15 | 15 | 0 | 0
L201H2 |  | SH201 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH2f-4 | S130074-02 | 13VS8224 | SH201-HUL12-DN350-P10 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 13 |  |  |  |  | 2022-05-31 | 72 | 64 | 8 | 61.5385 |  | 2022-07-08 | 77 | 77 | 0 | 0
L201H3 |  | SH201 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH3f-5 | S130074-02 | 13VS8225 | SH201-HUL12-DN350-P9 | - | 200 | 6.8kg/mm |  |  |  | 1150 kg | 1326 kg | 26 |  |  |  |  | 2022-05-31 | 76 | 71 | 5 | 19.2308 |  | 2022-07-08 | 100 | 98 | 2 | 7.4074
L201H4 |  | SH201 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH3A-6-M30 | S130074-02 | 13VS8223 | SH201-HUL13-DN350-P14 | - | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 31 |  |  |  |  | 2022-05-31 | 48 | 29 | 19 | 61.2903 |  | 2022-07-08 | 60 | 60 | 0 | 0
L202H1 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH1A-3-M16 | S130074-02 | 13VS8218 | SH202-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 363 kg | 418 kg | 8 |  |  |  |  | 2022-05-31 | 32 | 27 | 5 | 62.5 |  | 2022-07-08 | 35 | 35 | 0 | 0
L202H2 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH1A-5-M24 | S130074-02 | 13VS8221 | SH202-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1002 kg | 1220 kg | 8 |  |  |  |  | 2022-05-31 | 13 | 8 | 5 | 62.5 |  | 2022-07-08 | 17 | 17 | 0 | 0
L202H3 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | VH1A-6-M30 | S130074-02 | 13VS8222 | SH202-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 8 |  |  |  |  | 2022-05-31 | 15 | 14 | 1 | 12.5 |  | 2022-07-08 | 20 | 22 | 2 | 25
L202H4 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | CHH-32-B1A-100 | - | 13CS3837 | SH202-HUL21-DN350-AA25 | 2014-02 | 100 | - |  |  |  | 2658 kg | 2658 kg | 63 |  |  |  |  | 2022-05-31 | 71 | 82 | 11 | 17.4603 |  | 2022-07-08 | 11 | 19 | 8 | 12.6984
L202H5 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | CHH-32-B1A-100 | - | 13CS3836 | SH202-HUL21-DN350-AA19 | 2014-02 | 100 | - |  |  |  | 2431 kg | 2431 kg | 59 |  |  |  |  | 2022-05-31 | 62 | 79 | 17 | 28.8136 |  | 2022-07-08 | 16 | 20 | 4 | 6.7797
L202H6 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | CHH-20-B1A-120 | - | 13CS3835 | SH202-HUL21-DN350-AA21 | 2014-02 | 120 | - |  |  |  | 673 kg | 673 kg | 64 |  |  |  |  | 2022-05-31 | 69 | 83 | 14 | 21.875 |  | 2022-07-08 | 19 | 19 | 0 | 0
L202H7 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | CHH-34-B1A-120 | - | 13CS3838 | SH202-HUL23-DN350-AA24 | 2014-02 | 120 | - |  |  |  | 2336 kg | 2336 kg | 63 |  |  |  |  | 2022-05-31 | 71 | 81 | 10 | 15.873 |  | 2022-07-08 | 19 | 18 | 1 | 1.5873
L202H8 |  | SH202 |  |  |  |  | HRSG2 | [7 empty] | SEONGWHA | CHH-30-F1-130 | - | 14CS0356 | SH202-HUL26-DN350-AA23 | 2014-04 | 130 | - |  |  |  | 1656 kg | 1656 kg | 69 |  |  |  |  | 2022-05-31 | 63 | 69 | 6 | 8.6957 |  | 2022-07-08 | 0 | 0 | 0 | 0
Note on U15: Alex Horner: This suggests the hanger belongs on line 202 not 200. Hanger is mislabeled?
Note on R25: Alex Horner: Partially covered by paint, "20" is assumed based on other HRSGs
Note on T25: Alex Horner: Partially covered by paint, "13CS" Assumed from context
Note on U25: Alex Horner: Partially covered in paint "SH202" Assumed from context
Note on V25: Alex Horner: Partially covered by paint, "2014" assumed from context
Note on W25: Alex Horner: Partially covered by paint, "120" assumed from context and "Type"
Note on AB25: Alex Horner: Completely covered by paint, "673" assumed based on other HRSGs
Note on AC25: Alex Horner: Completely covered by paint, "673" assumed based on other HRSGs
Note on T26: Alex Horner: Partially covered by paint, "13CS" Assumed from context
Note on U26: Alex Horner: Partially covered in paint "SH202" Assumed from context
Note on T27: Alex Horner: Partially covered by paint, "13CS" Assumed from context
Note on U27: Alex Horner: Partially covered in paint "SH202" Assumed from context

## HRSG 3
[33 empty] | Hot walkdown | [5 empty] | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | % error | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % Error | Comments
L303H1 | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-22-B1A-60 | - | 13CS3823 | SH303-15CJ1G-H-C001 | 2013-02 | 60 | - |  |  |  | 1439 kg | 1439 kg | 28 |  |  |  |  | 2022-06-01 | 57 | 64 | 7 | 25 |  | 2022-07-02 | 38 | 36 | 2 | 7.1429
L303H2 | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 13CS3826 | SH303-15CJ1G-H-C002 | 2013-02 | 60 | - |  |  |  | 2064 kg | 2064 kg | 4 |  |  |  |  | 2022-06-01 | 40 | 49 | 9 | 225 |  | 2022-07-02 | 42 | 53 | 11
L303H3 | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-9-F1-60 | - | 14CS1109 | SH303-15CJ1G-H-C003 | 2014-05 | 60 | - |  |  |  | 400 kg | 400 kg | 54 |  |  |  |  | 2022-06-01 | 70 | 46 | 24 | 44.4444 |  | 2022-07-02 | 100 | 100 | 0
L303H4 | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-36-B1A-80 | - | 13CS3811 | SH303-15CJ1G-H-C004 | 2014-05 | 80 | - |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-06-01 | 50 | 40 | 10 | 50 |  | 2022-07-02 | 59 | 60 | 1
L303H5E | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | 14CS1108 | SH303-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-01 | 36 | 59 | 23 | 127.7778 |  | 2022-07-02 | 29 | 41 | 12
L303H5W | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG3 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | 14CS1107 | SH303-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-01 | 41 | 59 | 18 | 100 |  | 2022-07-02 | 31 | 41 | 10
L303H6 |  | SH303 |  |  |  |  | HRSG3 | [7 empty] | LISEGA | 215218 | 547404 | - | 630-SH380-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 14.1 kN | 7.92 |  |  |  |  | 2022-06-01 | 61 | 64 | 3 | 37.8788 |  | 2022-07-02 | 55 | 55 | 0
SNUBBER | 350-630-SH303-15CJ1G-H | SH303 | L630-DX-ISO-10528.001 | NO | 350-630-SH303-15CJ1G-H-X001 | V-2153-101-A-8006_002 | HRSG3 | MAIN STEAM | SNUBBER | [5 empty] | SANWA | [12 empty] | 0 |  |  |  |  | 2022-06-01 | [5 empty] | 2022-07-02 |  |  | 0
L315H1E | 300-630-SH315-15CJ1G-H | SH315 | V-2153-101-A-3006_004 | YES, 4 | 300-630-SH315-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG3 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1106 | SH315-15CJ1G-H-C001 | 2014-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-06-01 | 45 | 43 | 2 | 13.3333 |  | 2022-07-02 | 52 | 58 | 6
L315H1W | 300-630-SH315-15CJ1G-H | SH315 | V-2153-101-A-3006_004 | NO | 300-630-SH315-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG3 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1105 | SH315-15CJ1G-H-C001 | 2014-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-06-01 | 49 | 43 | 6 | 40 |  | 2022-07-02 | 55 | 58 | 3
L315H2 |  | SH315 |  |  |  |  | HRSG3 | [7 empty] | LISEGA | 215218 | 547404 | - | 630-SH383-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.52 kN | 7.58 |  |  |  |  | 2022-06-01 | 23 | 31 | 8 | 105.5409 |  | 2022-07-02 | 22 | 22 | 0
L315H3 |  | SH315 |  |  |  |  | HRSG3 | [7 empty] | LISEGA | 216218 | 547404 | - | 630-SH383-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.45 kN | 22.77 |  |  |  |  | 2022-06-01 | 66 | 87 | 21 | 92.2266 |  | 2022-07-02 | 64 | 64 | 0
L300H1 |  | SH300 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH2A-4-M20 | s130074-02 | 13VS8227 | SH302-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 16 |  |  |  |  | 2022-06-01 | 58 | 45 | 13 | 81.25 |  | 2022-07-02 | 63 | 63 | 0
L301H1 |  | SH301 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH1A-5-M24 | s130074-02 | 13VS8228 | SH301-HUL11-DN350-O02 | - | 50 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-06-01 | 9 | 14 | 5 | 166.6667 |  | 2022-07-02 | 9 | 11 | 2
L301H2 |  | SH301 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH2F-4 | s130074-02 | 13VS8232 | SH301-HUL12-DN350-O02 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 14 |  |  |  |  | 2022-06-01 | 76 | 67 | 9 | 64.2857 |  | 2022-07-02 | 81 | 81 | 0
L301H3 |  | SH301 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH3F-5 | s130074-02 | 13VS8233 | SH301-HUL12-DN350-P09 | - | 200 | 6.8 kg/mm |  |  |  | 1150 kg | 1326 kg | 29 |  |  |  |  | 2022-06-01 | 76 | 65 | 11 | 37.931 |  | 2022-07-02 | 88 | 94 | 6
L301H4 |  | SH301 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH3A-6-M30 | S130074-02 | 13VS8231 | SH301-HUL12-DN350-P14 | - | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 31 |  |  |  |  | 2022-06-01 | 40 | 22 | 18 | 58.0645 |  | 2022-07-02 | 45 | 54 | 9
L302H1 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH1A-3-M16 | S130074-02 | 13VS8226 | SH302-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 363 kg | 418 kg | 8 |  |  |  |  | 2022-06-01 | 32 | 25 | 7 | 87.5 |  | 2022-07-02 | 34 | 34 | 0
L302H2 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS8229 | SH302-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1220 kg | 1002 kg | 8 |  |  |  |  | 2022-06-01 | 17 | 9 | 8 | 100 |  | 2022-07-02 | 19 | 17 | 2
L302H3 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | VH1A-5-M30 | S130074-02 | 13VS8230 | SH302-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 8 |  |  |  |  | 2022-06-01 | 21 | 18 | 3 | 37.5 |  | 2022-07-02 | 21 | 26 | 5
L302H4 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3841 | SH302-HUL21-DN350-AA25 | 2014-02 | 100 | - |  |  |  | 2658 kg | 2658 kg | 61 |  |  |  |  | 2022-06-01 | 78 | 81 | 3 | 4.918 |  | 2022-07-02 | 19 | 20 | 1
L302H5 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3840 | SH302-HUL21-DN350-AA19 | 2014-02 | 100 | - |  |  |  | 2431 kg | 2431 kg | 59 |  |  |  |  | 2022-06-01 | 68 | 79 | 11 | 18.6441 |  | 2022-07-02 | 26 | 20 | 6
L302H6 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | CHH-20-B1A-120 | - | 13CS3839 | SH302-HUL21-DN350-AA21 | 2014-02 | 120 | - |  |  |  | 673 kg | 673 kg | 63 |  |  |  |  | 2022-06-01 | 71 | 82 | 11 | 17.4603 |  | 2022-07-02 | 21 | 19 | 2
L302H7 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | CHH-34-B1A-120 | - | 13CS3842 | SH302-HUL23-DN350-AA24 | 2014-02 | 120 | - |  |  |  | 2336 kg | 2336 kg | 63 |  |  |  |  | 2022-06-01 | 78 | 81 | 3 | 4.7619 |  | 2022-07-02 | 19 | 18 | 1
L302H8 |  | SH302 |  |  |  |  | HRSG3 | [7 empty] | SEONGHWA | CHH-30-F1-130 | - | 14CS0357 | SH302-HUL26-DN350-AA23 | 2014-02 | 130 | - |  |  |  | 1656 kg | 1656 kg | 69 |  |  |  |  | 2022-06-01 | 72 | 69 | 3 | 4.3478 |  | 2022-07-02 | 0 | 0 | 0
Note on U9: Alex Horner: Plate scratched, value assumed from other HRSGs
Note on U15: Alex Horner: This suggests the hanger belongs on line 302 not 300. Hanger is mislabeled?
Note on U21: Alex Horner: Patially covered by paint, "DN250" assumed from context

## HRSG 4
|  |  | Assumption: All HRSGs share isometric drawings |  |  | Assumption: All HRSGs share isometric drawings | [26 empty] | Hot walkdown | [5 empty] | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | % error | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % Error | Comments
L403H1 | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 4 | 350-630-SH403-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-22-B1A-60 | - | 13CS3587 | SH403-15CJ1G-H-C001 | 2014-01 | 60 | - |  |  |  | 1439 kg | 1439 kg | 28 |  |  |  |  | 2022-06-01 | 46 | 64 | 18 | 64.2857 |  | 2022-07-09 | 34 | 36 | 2 | 7.1429
L403H2 | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH403-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 13CS3590 | SH403-15CJ1G-H-C002 | 2014-01 | 60 | - |  |  |  | 2064 kg | 2064 kg | 2 |  |  |  |  | 2022-06-01 | 23 | 50 | 27 | 1350 |  | 2022-07-09 | 37 | 52 | 15 | 750
L403H3 | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH403-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-9-F1-60 | - | 14CS1114 | SH403-15CJ1G-H-C003 | 2014-05 | 60 | - |  |  |  | 400 kg | 400 kg | 52 |  |  |  |  | 2022-06-01 | 100 | 48 | 52 | 100 |  | 2022-07-09 | 100 | 100 | 0 | 0
L403H4 | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | NO | 350-630-SH403-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-36-B1A-80 | - | 13CS3593 | SH403-15CJ1G-H-C004 | 2014-05 | 80 |  |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-06-01 | 70 | 40 | 30 | 150 |  | 2022-07-09 | 60 | 60 | 0 | 0
L403H5E | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 22 | 350-630-SH403-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | 14CS1112 | SH403-15CJ1G-H-C005 | 2014-05 | 60 |  |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-01 | 69 | 59 | 10 | 55.5556 |  | 2022-07-09 | 45 | 41 | 4 | 22.2222
L403H5W | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 15 | 350-630-SH403-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG4 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | 14CS1113 | SH403-15CJ1G-H-C005 | 2014-05 | 60 |  |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-01 | 80 | 59 | 21 | 116.6667 |  | 2022-07-09 | 51 | 41 | 10 | 55.5556
L403H6 | [14 empty] | LISEGA | 215218 | 5474057 | - | 630-SH480-PS-0 | - | 100 | 133.3 N/mm |  |  |  | - | 14.03 kN | 7.9 |  |  |  |  | 2022-06-01 | 69 | 61 | 8 | 101.2658 |  | 2022-07-09 | 56 | 54 | 2 | 28.5714
SNUBBER | 350-630-SH403-15CJ1G-H | SH403 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH403-15CJ1G-H-X001 | V-2153-101-A-8006_002 | HRSG4 | MAIN STEAM | SNUBBER | [23 empty] | 2022-06-01 | [5 empty] | 2022-07-09
L415H1E | 300-630-SH415-15CJ1G-H | SH415 | V-2153-101-A-3006_004 | YES, 3 | 300-630-SH415-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG4 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1110 | SH415-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 17 |  |  |  |  | 2022-06-01 | 68 | 42 | 26 | 152.9412 |  | 2022-07-09 | 50 | 59 | 9 | 52.9412
L415H1W | 300-630-SH415-15CJ1G-H | SH415 | V-2153-101-A-3006_004 | YES, 15 | 300-630-SH415-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG4 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1111 | SH415-15CJ1G-H-C001 | 2014-05 | 60 |  |  |  |  | 1841 kg | 1841 kg | 17 |  |  |  |  | 2022-06-01 | 68 | 42 | 26 | 152.9412 |  | 2022-07-09 | 44 | 59 | 15 | 88.2353
L415H2 |  | SH415 |  |  |  |  | HRSG4 | [7 empty] | LISEGA | 215218 | 5474057 | - | 630-SH483-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.530kN | 7.6 |  |  |  |  | 2022-06-01 | 28 | 24 | 4 | 52.6316 |  | 2022-07-09 | 27 | 17 | 10 | 142.8571
L415H3 |  | SH415 |  |  |  |  | HRSG4 | [7 empty] | LISEGA | 216218 | 547404 |  | 630-SH483-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.48kN | 22.77 |  |  |  |  | 2022-06-01 | 67 | 87 | 20 | 87.8349 |  | 2022-07-09 | 61 | 62 | 1 | 4
L400H1 |  | SH400 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH2A-4-M20 | s130074-02 | 13VS7692 | SH402-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 16 |  |  |  |  | 2022-06-01 | 58 | 49 | 9 | 56.25 |  | 2022-07-09 | 64 | 65 | 1 | 6.25
L401H1 |  | SH401 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH1A-5-M24 | s130074-02 | 13VS7693 | SH401-HUL11-DN350-O02 | - | 50 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-06-01 | 11 | 9 | 2 | 66.6667 |  | 2022-07-09 | 13 | 13 | 0 | 0
L401H2 |  | SH401 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH2F-4 | s130074-02 | 13VS7697 | SH401-HUL12-DN350-P10 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 13 |  |  |  |  | 2022-06-01 | 80 | 71 | 9 | 69.2308 |  | 2022-07-09 | 84 | 84 | 0 | 0
L401H3 |  | SH401 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH3F-5 | s130074-02 | 13VS7698 | SH401-HUL12-DN350-P09 | - | 200 | 6.8 kg/mm |  |  |  | 1150 kg | 1326 kg | 26 |  |  |  |  | 2022-06-01 | 85 | 74 | 11 | 42.3077 |  | 2022-07-09 | 99 | 100 | 1 | 3.8462
L401H4 |  | SH401 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH3A-6-M30 | S130074-02 | 13VS7696 | SH401-HUL13-DN350-P014 |  | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 31 |  |  |  |  | 2022-06-01 | 41 | 24 | 17 | 54.8387 |  | 2022-07-09 | 52 | 55 | 3 | 9.6774
L402H1 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH1A-3-M16 | S130074-02 | 13VS7691 | SH402-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 363 kg | 418 kg | 8 |  |  |  |  | 2022-06-01 | 34 | 30 | 4 | 50 |  | 2022-07-09 | 34 | 38 | 4 | 50
L402H2 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS7694 | SH402-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1220 kg | 1002 kg | 8 |  |  |  |  | 2022-06-01 | 15 | 11 | 4 | 50 |  | 2022-07-09 | 14 | 19 | 5 | 62.5
L402H3 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | VH1A-5-M30 | S130074-02 | 13VS7695 | SH402-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 8 |  |  |  |  | 2022-06-01 | 25 | 17 | 8 | 100 |  | 2022-07-09 | 23 | 25 | 2 | 25
L402H4 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3606 | SH402-HUL21-DN350-AA25 | 2013-01 | 100 | - |  |  |  | 2658 kg | 2658 kg | 62 |  |  |  |  | 2022-06-01 | 74 | 81 | 7 | 11.2903 |  | 2022-07-09 | 19 | 19 | 0 | 0
L402H5 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3605 | SH402-HUL21-DN350-AA19 | 2013-01 | 100 | - |  |  |  | 2431 kg | 2431 kg | 59 |  |  |  |  | 2022-06-01 | 87 | 79 | 8 | 13.5593 |  | 2022-07-09 | 26 | 20 | 6 | 10.1695
L402H6 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | CHH-20-B1A-120 | - | 13CS3604 | SH402-HUL21-DN350-AA21 | 2013-01 | 120 | - |  |  |  | 673 kg | 673 kg | 64 |  |  |  |  | 2022-06-01 | 85 | 83 | 2 | 3.125 |  | 2022-07-09 | 21 | 19 | 2 | 3.125
L402H7 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | CHH-34-B1A-120 | - | 13CS3607 | SH402-HUL23-DN350-AA24 | 2013-01 | 120 | - |  |  |  | 2336 kg | 2336 kg | 64 |  |  |  |  | 2022-06-01 | 73 | 81 | 8 | 12.5 |  | 2022-07-09 | 19 | 17 | 2 | 3.125
L402H8 |  | SH402 |  |  |  |  | HRSG4 | [7 empty] | SEONGHWA | CHH-30-F1-130 | - | 13CS3612 | SH402-HUL26-DN350-AA23 | 2014-02 | 130 | - |  |  |  | 1656 kg | 1656 kg | 68 |  |  |  |  | 2022-06-01 | 70 | 68 | 2 | 2.9412 |  | 2022-07-09 | 1 | 0 | 1 | 1.4706
Note on U15: Alex Hopp: This suggests the hanger belongs on line 402 not 400. Hanger is mislabeled?

## HRSG 5
[33 empty] | Hot walkdown | [5 empty] | Cold walkdown
Temporary Support Number | Line number | Group | Piping drawing | Multiple sheets | Support number | Support drawing | Location | Description | Type | Accessible | Defect | Description | Action | Comment | Manufacturer | Type | Model - Size | Serial No | ID No. | Date Installed | Travel Limit (mm) | Spring Rate | Level | RL | Moment Arm (mm) | Design Load (Hot) | Design Load (Cold) | Design Travel (mm) | Pipe Design Pressure | Pipe Design Temperature | Pipe OD | Pipe Wall Thickness | Date | Hot Position (mm) | Hot Design (mm) | Distance from Design (mm) | % error | Comments | Date | Cold Position (mm) | Cold Design (mm) | Distance from Design (mm) | % Error | Comments
L503H1 | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | YES, 7 | 350-630-SH503-15CJ1G-H-C001 | V-2153-101-A-8006_001 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-22-B1A-60 | - | 13CS3596 | SH503-15CJ1G-H-C001 | 2014-01 | 60 | - |  |  |  | 1439 kg | 1439 kg | 28 |  |  |  |  | 2022-06-02 | 47 | 64 | 17 | 60.7143 |  | 2022-07-09 | 36 | 36 | 0 | 0
L503H2 | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH503-15CJ1G-H-C002 | V-2153-101-A-8006_003 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 13CS3599 | SH503-15CJ1G-H-C002 | 2014-01 | 60 | - |  |  |  | 2064 kg | 2064 kg | 3 |  |  |  |  | 2022-06-02 | 31 | 49 | 18 | 600 |  | 2022-07-09 | 42 | 52 | 10 | 333.3333
L503H3 | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | NO | 350-630-SH503-15CJ1G-H-C003 | V-2153-101-A-8006_004 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-9-F1-60 | - | 14CS1119 | SH503-15CJ1G-H-C003 | 2014-06 | 60 | - |  |  |  | 400 kg | 400 kg | 54 |  |  |  |  | 2022-06-02 | 100 | 46 | 54 | 100 |  | 2022-07-09 | 100 | 100 | 0 | 0
L503H4 | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | NO | 350-630-SH503-15CJ1G-H-C004 | V-2153-101-A-8006_005 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-36-B1A-80 | - | 13CS3602 | SH503-15CJ1G-H-C004 | 2014-05 | 80 | - |  |  |  | 4876 kg | 4876 kg | 20 |  |  |  |  | 2022-06-02 | 74 | 40 | 34 | 170 |  | 2022-07-09 | 61 | 60 | 1 | 5
L503H5E | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | YES, 7 | 350-630-SH503-15CJ1G-H-C005 | V-2153-101-A-8006_006 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | 14CS1117 | SH503-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-02 | 93 | 59 | 34 | 188.8889 |  | 2022-07-09 | 60 | 41 | 19 | 105.5556
L503H5W | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | NO | 350-630-SH503-15CJ1G-H-C005 | V-2153-101-A-8006_007 | HRSG5 | MAIN STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-28-B1A-60 | - | HEAVY SCRATCHING | SH503-15CJ1G-H-C005 | 2014-05 | 60 | - |  |  |  | 2883 kg | 2883 kg | 18 |  |  |  |  | 2022-06-02 | 95 | 59 | 36 | 200 |  | 2022-07-09 | 59 | 41 | 18 | 100
L503H6 | [6 empty] | HRSG5 | MAIN STEAM | [6 empty] | LISEGA | 215218 | 5474057 | - | 630-SH580-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 14.03 kN | 7.9 |  |  |  |  | 2022-06-02 | 66 | 57 | 9 | 113.9241 |  | 2022-07-09 | 52 | 50 | 2 | 28.5714
SNUBBER | 350-630-SH503-15CJ1G-H | SH503 | L630-DX-ISO-10528.001 | YES, 3 | 350-630-SH503-15CJ1G-H-X001 | V-2153-101-A-8006_002 | HRSG5 | MAIN STEAM | SNUBBER | [5 empty] | SANWA | [12 empty] | 0 |  |  |  |  | 2022-06-02 | [5 empty] | 2022-07-09
L515H1E | 300-630-SH515-15CJ1G-H | SH515 | V-2153-101-A-3006_004 | YES, 11 | 300-630-SH515-15CJ1G-H-C001 | V-2153-101-A-8006_013 | HRSG5 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1115 | SH515-15CJ1G-H-C001 | 2014-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-06-02 | 68 | 43 | 25 | 166.6667 |  | 2022-07-09 | 49 | 58 | 9 | 60
L515H1W | 300-630-SH515-15CJ1G-H | SH515 | V-2153-101-A-3006_004 | NO | 300-630-SH515-15CJ1G-H-C001 | V-2153-101-A-8006_014 | HRSG5 | BYPASS STEAM | SPRING HANGER - CONSTANT | [5 empty] | SEONGHWA | CHH-24-B1A-60 | - | 14CS1116 | SH515-15CJ1G-H-C001 | 2015-05 | 60 | - |  |  |  | 1841 kg | 1841 kg | 15 |  |  |  |  | 2022-06-02 | 69 | 43 | 26 | 173.3333 |  | 2022-07-09 | 49 | 58 | 9 | 60
L515H2 |  | SH515 |  |  |  |  | HRSG5 | [7 empty] | LISEGA | 215218 | 5474057 | - | 630-SH583-PS-0-001 | - | 100 | 133.3 N/mm |  |  |  | - | 9.4 kN | 8.5 |  |  |  |  | 2022-06-02 | 26 | 24 | 2 | 23.5294 |  | 2022-07-09 |  | 17 | 17 | 242.8571
L515H3 |  | SH515 |  |  |  |  | HRSG5 | [7 empty] | LISEGA | 216218 | 547404 | - | 630-SH583-PS-0-005 | - | 100 | 266.6 N/mm |  |  |  | - | 29.48 kN | 22.77 |  |  |  |  | 2022-06-02 | 71 | 87 | 16 | 70.2679 |  | 2022-07-09 | 55 | 64 | 9 | 39.1304
L500H1 |  | SH500 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH2A-4-M20 | S130074-02 | 13VS7700 | SH502-HUL05-DN250-A02 | - | 100 | 6.8 kg/mm |  |  |  | 698 kg | 807 kg | 16 |  |  |  |  | 2022-06-02 | 51 | 43 | 8 | 50 |  | 2022-07-09 | 56 | 61 | 5 | 27.7778
L501H1 |  | SH501 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS7701 | SH501-HUL11-DN350-O02 | - | 50 | 27.2 kg/mm |  |  |  | 993 kg | 1074 kg | 3 |  |  |  |  | 2022-06-02 | 9 | 6 | 3 | 100 |  | 2022-07-09 | 11 | 9 | 2 | 66.6667
L501H2 |  | SH501 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH2F-4 | S130074-02 | 13VS7705 | SH501-HUL12-DN350-P10 | - | 100 | 6.8 kg/mm |  |  |  | 866 kg | 954 kg | 13 |  |  |  |  | 2022-06-02 | 86 | 72 | 14 | 107.6923 |  | 2022-07-09 | 79 | 86 | 7 | 50
L501H3 |  | SH501 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH3F-5 | S130074-02 | 13VS7706 | SH501-HUL12-DN350-P9 | - | 200 | 6.8 kg/mm |  |  |  | 1150 kg | 1326 kg | 26 |  |  |  |  | 2022-06-02 | 89 | 69 | 20 | 76.9231 |  | 2022-07-09 | 91 | 95 | 4 | 15.3846
L501H4 |  | SH501 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH3A-6-M30 | S130074-02 | 13VS7704 | SH501-HUL13-DN350-14 | - | 200 | 13.6 kg/mm |  |  |  | 1792 kg | 2213 kg | 31 |  |  |  |  | 2022-06-02 | 41 | 25 | 16 | 51.6129 |  | 2022-07-09 | 52 | 56 | 4 | 12.9032
L502H1 |  | SH502 |  |  |  |  | HRSG5 | [6 empty] | * Hanger names may swap if hangers are relocated to correct positions | SEONGHWA | VH1A-5-M24 | S130074-02 | 13VS7702 | SH502-HUL17-DN250-W06 | - | 50 | 27.2 kg/mm |  |  |  | 1220 kg | 1002 kg | 8 |  |  |  |  | 2022-06-02 | 13 | 11 | 2 | 25 |  | 2022-07-09 | 17 | 20 | 3 | 33.3333
L502H2 |  | SH502 |  |  |  |  | HRSG5 | [6 empty] | * Hanger names may swap if hangers are relocated to correct positions | SEONGHWA | VH1A-3-M16 | S130074-02 | 13VS7699 | SH502-HUL17-DN250-X06 | - | 50 | 6.8 kg/mm |  |  |  | 363 kg | 418 kg | 8 |  |  |  |  | 2022-06-02 | 27 | 26 | 1 | 12.5 |  | 2022-07-09 | 31 | 34 | 3 | 37.5
L502H3 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | VH1A-5-M30 | S130074-02 | 13VS7703 | SH502-HUL21-DN350-AA17 | - | 50 | 54.4 kg/mm |  |  |  | 2686 kg | 3121 kg | 8 |  |  |  |  | 2022-06-02 | 28 | 18 | 10 | 125 |  | 2022-07-09 | 21 | 26 | 5 | 62.5
L502H4 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3610 | SH502-HUL21-DN350-AA25 | 2013-01 | 100 | - |  |  |  | 2658 kg | 2658 kg | 63 |  |  |  |  | 2022-06-02 | 75 | 82 | 7 | 11.1111 |  | 2022-07-09 | 24 | 19 | 5 | 7.9365
L502H5 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | CHH-32-B1A-100 | - | 13CS3609 | SH502-HUL21-DN350-AA19 | 2013-01 | 100 | - |  |  |  | 2431 kg | 2431 kg | 60 |  |  |  |  | 2022-06-02 | 60 | 79 | 19 | 31.6667 |  | 2022-07-09 | 20 | 19 | 1 | 1.6667
L502H6 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | CHH-20-B1A-120 | - | 13CS3608 | SH502-HUL21-DN350-AA21 | 2013-01 | 120 | - |  |  |  | 673 kg | 673 kg | 65 |  |  |  |  | 2022-06-02 | 65 | 83 | 18 | 27.6923 |  | 2022-07-09 | 21 | 18 | 3 | 4.6154
L502H7 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | CHH-34-B1A-120 | - | SCRATCHED PLATE | SH502-HUL23-DN350-AA24 | 2013-01 | 120 | - |  |  |  | 2336 kg | 2336 kg | 63 |  |  |  |  | 2022-06-02 | 76 | 81 | 5 | 7.9365 |  | 2022-07-09 | 20 | 18 | 2 | 3.1746
L502H8 |  | SH502 |  |  |  |  | HRSG5 | [7 empty] | SEONGHWA | CHH-30-F1-130 | - | 13CS3613 | SH502-HUL26-DN350-AA23 | 2014-02 | 130 | - |  |  |  | 1656 kg | 1656 kg | 69 |  |  |  |  | 2022-06-02 | 71 | 69 | 2 | 2.8986 |  | 2022-07-09 | 1 | 0 | 1 | 1.4493
Note on R3: Alex Horner: Plate extremely scratched, Value assumed from context/other HRSGs
Note on U3: Alex Horner: Plate extremely scratched, Value assumed from context/other HRSGs
Note on V3: Alex Horner: Plate extremely scratched, Value assumed from context/other HRSGs
Note on AB8: Alex Horner: Heavy scratching, assumed from context
Note on AC8: Alex Horner: Heavy scratching, assumed from context
Note on U11: Alex Horner: Plate extremely scratched, Value assumed from context/other HRSGs
Note on AB11: Alex Horner: Value assumed from context, scracthed plate
Note on AC11: Alex Horner: Value assumed from context, scracthed plate
Note on AB12: Alex Horner: Value assumed from context, scracthed plate
Note on AC12: Alex Horner: Value assumed from context, scracthed plate
Note on A20: Alex Horner: Hangers are suspected to have been installed incorrectly (swapped)
Note on A21: Alex Horner: Hangers are suspected to have been installed incorrectly (swapped)
Note on V26: Alex Horner: Month assumed from context, scratched plate
Note on R27: Alex Horner: Assumed value based on other HRSGs, scratched plate
Note on U27: Alex Horner: Assumed value based on other HRSGs, scratched plate